## Slide 1
ECE 1710: Power Distribution Engineering and Smart Grids
Lecture 6
Dr. Robert Kerestes
University of Pittsburgh
Swanson School of Engineering
Department of Electrical and Computer Engineering
Notes: Instructions for editing school and department titles:
Select from menu: View > Master > Slide Master
Click on each text area you wish to edit. Text will become editable.

## Slide 2: Outline
Module #1: Primitive and Phase Impedance Matrices for Overhead Lines
Module #2: Parallel Overhead Lines
Module #3: Parallel Overhead Lines
Lecture Outline

## Slide 3
Learning Objectives:
  Define the primitive impedance matrix for a transmission line
  Reduce primitive impedance and potential coefficient matrices using Kron reduction
  Calculate phase impedance and shunt admittance matrices using Kron reduction
  Write the matrix equation for voltage drop across a transmission line
Learning Objectives

## Slide 4: Primitive and Phase Impedance Matrix for Overhead Lines

## Slide 5: Series Impedance of Overhead Lines
The general form of a primitive impedance matrix with m neutrals is

## Slide 6: Series Impedance of Overhead Lines
An overhead four-wire grounded wye distribution line segment will result in a 4 × 4 matrix

## Slide 7: Series Impedance of Overhead Lines
In partitioned form the matrix becomes:
where:

## Slide 8: Series Impedance of Overhead Lines
The submatrices for the 4 x 4 are shown in the color coded squares below
where:

## Slide 9: Series Impedance of Overhead Lines
The primitive impedance matrix usually has to be reduced to a 3 x 3 “phase impedance matrix”:
Which is called the Kron reduction technique, giving us

## Slide 10: Series Impedance of Overhead Lines
Gabriel Kron
1901-1968
Electrical Engineer
University of Michigan
General Electric
Gabriel Kron was a Hungarian-American electrical engineer who promoted the use of methods of linear algebra, multilinear algebra, and differential geometry in the field.

## Slide 11: Series Impedance of Overhead Lines
This method can be used to solve the following system:

## Slide 12: Series Impedance of Overhead Lines
With phase impedance matrices:
and:
where

## Slide 13: Series Impedance of Overhead Lines
If a line is not transposed:
  The diagonal elements will not be equal to each other
  The off-diagonal elements will not be equal to each other
V phase and single phase connected laterals can be reduced using Kron reduction in wye-connected grounded systems
  V phase have 3 x 3 primitive impedance matrices, which are reduced to 2 x 2 using Kron reduction
  Single phase have 2 x 2 primitive impedance matrices, which are reduced to single element using Kron reduction

## Slide 14: Series Impedance of Overhead Lines
For example, for a V-phase line consisting of phases a and c, the phase impedance matrix would be:
The phase impedance matrix for a phase b single-phase line would be:

## Slide 15: Series Impedance of Overhead Lines
The phase impedance matrix for a three-wire delta line is determined by the application of Carson's equations without the Kron reduction step.
Finally, we have the three phase line segment model using Kron reduction for wye-connected circuits, and leaving delta connected circuits in their primitive impedance matrix form.

## Slide 16: Series Impedance of Overhead Lines
The voltage equation for a line segment is then:
Or in condense form:

## Slide 17
Parallel Overhead Lines

## Slide 18: Parallel Overhead Lines
It is fairly common in a distribution system to find instances where two distribution lines are “physically” parallel.
The parallel combination may have both distribution lines constructed on the same pole, or the two lines may run in parallel on separate poles but on the same right-of-way.
For example, two different feeders leaving a substation may share a common pole or right-of-way before they branch out to their own service area. analyzed.

## Slide 19: Parallel Overhead Lines
Two parallel lines are shown below. Note that these lines share one common neutral.

## Slide 20: Parallel Overhead Lines
For this example, a 7 x 7 matrix would be produced where

## Slide 21: Parallel Overhead Lines
Which can be partitioned

## Slide 22: Parallel Overhead Lines
Then using the Kron reduction we have

## Slide 23: Parallel Overhead Lines
And the voltage drop equation will be

## Slide 24: Concentric Neutral Cable
Module #1

## Slide 25: Concentric Neutral Cable
Module #1
Shown below is the general configuration of three underground cables (concentric neutral or tape-shielded) with an additional neutral conductor.

## Slide 26: Concentric Neutral Cable
Module #1
There are two popular types of underground cables
Concentric neutral cable
Tape shield cable

## Slide 27: Concentric Neutral Cable
Module #1
There are two popular types of underground cables
Concentric neutral cable
Tape shield cable
Underground circuits will produce a 7 x 7 primitive impedance matrix if there is a neutral and a 6 x 6 if there is not a neutral

## Slide 28: Concentric Neutral Cable
Module #1
Shown below is a drawing of a concentric neutral cable

## Slide 29: Concentric Neutral Cable
Module #1
In order to apply Carson’s equations to this cable, the following data needs to be extracted from a table of underground cables (Appendices A and B).
dc = phase conductor diameter (in.)
dod = nominal diameter over the concentric neutrals of the cable (in.)
ds = diameter of a concentric neutral strand (in.)
GMRc = geometric mean radius of the phase conductor (ft)
GMRs = geometric mean radius of a neutral strand (ft)
rc = resistance of the phase conductor (Ω/mile)
rs = resistance of a solid neutral strand (Ω/mile)
k = number of concentric neutral strands

## Slide 30
Module #1

## Slide 31: Concentric Neutral Cable
Module #1
The GMRs of the phase conductor and a neutral strand are obtained from a standard table of conductor data (Appendix A).
The equivalent GMR of the concentric neutral is computed using the equation for the GMR of bundled conductors used in high-voltage transmission lines:

## Slide 32: Concentric Neutral Cable
Module #1
R = radius of a circle passing through the center of the concentric neutral strands
The equivalent resistance of the concentric neutral is:

## Slide 33: Concentric Neutral Cable
Module #1
The various spacings between a concentric neutral and the phase conductors and other concentric neutrals are as follows:
Concentric Neutral to Its Own Phase Conductor:
Concentric Neutral to an Adjacent Concentric Neutral:

## Slide 34: Concentric Neutral Cable
Module #1
Concentric Neutral to an Adjacent Phase Conductor

## Slide 35: Concentric Neutral Cable
Module #1
The distance between cables will be much greater than the radius R; so a good approximation of modeling the concentric neutral cables is shown in below. In this figure, the concentric neutrals are modeled as one equivalent conductor (shown in black) directly above the phase conductor.

## Slide 36: Concentric Neutral Cable
Module #1
n applying the Modified Carson’s Equations, the numbering of conductors and neutrals is important. For example, a three-phase underground circuit with an additional neutral conductor must be numbered as:
1 = phase a Conductor #1
2 = phase b Conductor #2
3 = phase c Conductor #3
4 = neutral of Conductor #1
5 = neutral of Conductor #2
6 = neutral of Conductor #3
7 = additional neutral conductor (if present)

## Slide 37: Concentric Neutral Cable
Module #1
Recall modified Carson’s equations are:

## Slide 38: Concentric Neutral Example
Module #2
Three concentric neutral cables are buried in a trench with spacings as shown in the figure below
The cables are 15 kV, 250,000 CM stranded all aluminum with k = 13 strands of #14 annealed coated copper wires (1/3 neutral). The outside diameter of the cable over the neutral strands is 1.29 in. Determine the phase impedance matrix and the sequence impedance matrix.

## Slide 39: Concentric Neutral Example
Module #2
The equivalent model for these cables is shown below

## Slide 40
Module #2

## Slide 41
Module #2

## Slide 42
Module #2

## Slide 43: Concentric Neutral Example
Module #2
The data for the phase and neutral conductors is

## Slide 44: Concentric Neutral Example
Module #2
We then can calculate radius of the circle passing through the center of the strands
Then using that to calculate the equivalent GMR

## Slide 45: Concentric Neutral Example
Module #2
Calculating the equivalent resistance for the concentric neutral conductor

## Slide 46: Concentric Neutral Example
Module #2
The coordinates for the conductors can be defined where the center of the phase conductors are at a y-coordinate of 0. Centering the center conductor
(0,0)
(-0.5,0)
(0.5,0)

## Slide 47: Concentric Neutral Example
Module #2
The neutrals use the equivalent resistance and equivalent GMR are used for the concentric neutrals.
Modified Carson’s equations can then be used to solve for the impedance elements of the primitive impedance matrix.

## Slide 48: Concentric Neutral Example
Module #2
Below is the output of a MATLAB Script which calculates the primitive impedance matrix.

## Slide 49: Concentric Neutral Example
Module #2
Applying the Kron reduction yields

## Slide 50
Module #3
Tape-Shielded Cables

## Slide 51: Tape-Shielded Cables
Module #3
The figure below shows a simple detail of a tape-shielded cable.

## Slide 52: Tape-Shielded Cables
Module #3
For the tape shielded cable

## Slide 53: Tape-Shielded Cables
Module #3
The resistance of the tape shield is given by:
This resistance of the tape shield given assumes a resistivity (ρm20) of 1.7721 · 10−8 Ω-m and a temperature of 20°C. The outside diameter of the tape shield ds is given in inches, and the thickness of the tape shield T is in mils.

## Slide 54: Tape-Shielded Cables
Module #3
The GMR of the tape shield is the radius of a circle passing through the middle of the shield and is given by:

## Slide 55: Tape-Shielded Cables
Module #3
Tape Shield to its Own Phase Conductor
Tape Shield to an Adjacent Tape Shield
Tape Shield to an Adjacent Phase or Neutral Conductor
where Dnm = center-to-center distance between phase conductors.

## Slide 56: Tape-Shielded Cables
Module #3
Example: A single-phase circuit consists of a 1/0 AA, 220 mil insulation tape-shielded cable and a 1/0 CU neutral conductor. The single-phase line is connected to phase b. Determine the phase impedance matrix.

## Slide 57: Tape-Shielded Cables
Module #3

## Slide 58: Tape-Shielded Cables
Module #3

## Slide 59: Tape-Shielded Cables
Module #3
For the phase conductor

## Slide 60: Tape-Shielded Cables
Module #3

## Slide 61: Tape-Shielded Cables
Module #3
For the neutral

## Slide 62: Tape-Shielded Cables
Module #3
The basic calculations are:
Resistance of the tape shield
GMR of the tape shield

## Slide 63: Tape-Shielded Cables
Module #3
The conductors are numbered such that:
#1 = 1/0 AA conductor
#2 = tape shield
#3 = 1/0 copper ground

## Slide 64: Tape-Shielded Cables
Module #3
Then just use Carson’s equations to get
Partitioned as

## Slide 65: Tape-Shielded Cables
Module #3
And performing the Kron reduction

## Slide 66: Tape-Shielded Cables
Module #3
And finally the phase matrix, will only have one row and one column of non-zero values

## Slide 67: Tape-Shielded Cables
Module #3
Question: The tape thickness for a tape-shielded cable in general is equal to
0.005 inches
0.05 inches
0.5 inches
5 inches
None of the above

## Slide 68
Module #4
Parallel Underground Lines

## Slide 69: Parallel Underground Lines
Module #4
The procedure for computing the phase impedance matrix for two overhead parallel lines has been presented in a previous lection. The figure below two concentric neutral parallel lines each with a separate grounded neutral conductor.

## Slide 70: Parallel Underground Lines
Module #4
The same process for calculating parallel overhead lines would be used, however this would result in a 14 x 14 primitive impedance matrix

## Slide 71: Parallel Underground Lines
Module #4
After the Kron reduction is performed, the following matrix would be produced

## Slide 72: Parallel Underground Lines
Module #4
Or equivalently

## Slide 73: Parallel Underground Lines
Module #4
Question: The size of the primitive impedance matrix for the following set of parallel underground lines is _____ x _____

## Slide 74: Parallel Underground Lines
Module #4
Question: After the Kron reduction is produced, the size of the phase impedance matrix for the following set of parallel underground lines is _____ x _____